## RS0003
RS0003: Fan Assembly
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0003 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | Continuous Fan |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-11T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
description
description.product_information
| manufacturer | ABC Fans
| model_number | Cont 1a2b
| impeller_type | CENTRIFUGAL_AIR_FOIL
performance |  |  |  | ✓
| nominal_standard_air_volumetric_flow_rate | 9.5 | m3/s | ✓
| is_enclosed | FALSE |  | ✓
| assembly_components | $assembly_components
| heat_loss_fraction | 1 | - | ✓
| maximum_impeller_rotational_speed | 28 | rev/s | ✓
| minimum_impeller_rotational_speed | 15 | rev/s | ✓
performance.stability_curve
| standard_air_volumetric_flow_rate | $standard_air_volumetric_flow_ra | m3/s | ✓
| static_pressure_difference | $static_pressure_difference | Pa | ✓
| operation_speed_control_type | CONTINUOUS |  | ✓
| installation_speed_control_type | FIXED |  | ✓
performance.performance_map |  | $performance_map |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on A12: Data group describing product and rating information
Note on A13: Data group describing product information
Note on B14: Assembly/unit manufacturer name
Note on B15: Assembly/unit model number
Note on B16: Type of impeller in fan assembly
Note on A17: Data group containing performance information
Note on B18: Nominal or rated air flow rate at standard air conditions
Note on B19: Fan assembly is enclosed
Note on B20: An array of components included in the fan assembly air stream, not including any fans
Note on B21: Fraction of efficiency losses transferred into the air stream
Note on B22: Maximum impeller rotational speed
Note on B23: Minimum impeller rotational speed
Note on A24: The system curve defining the stability area for system selection
Note on B25: Volumetric air flow rate through an air distribution system at standard air conditions
Note on B26: Static pressure difference of an air distribution system
Note on B27: Type of performance map
Note on B28: Type of fan impeller speed control
Note on A29: Data group describing fan assembly performance when operating

## assembly_components
performance.assembly_components
assembly_components

## standard_air_volumetric_flow_ra
performance.stability_curve.standard_air_volumetric_flow_rate
standard_air_volumetric_flow_rate
m3/s
0
0.0009439
0.0028317
0.0047195
0.0066073
0.0084951
0.010383
0.012271

## static_pressure_difference
performance.stability_curve.static_pressure_difference
static_pressure_difference
Pa
0
32.4985
118.9953
258.0471
478.3202
808.4812
1277.1962
1913.1317

## performance_map
performance.performance_map
grid_variables |  | lookup_variables
standard_air_volumetric_flow_rate | static_pressure_difference | impeller_rotational_speed | shaft_power
m3/s | Pa | rev/s | W
5.6634 | 622.1 | 15.1333 | 4690.453
5.6634 | 746.52 | 16 | 5480.895
5.6634 | 870.94 | 16.8167 | 6293.708
5.6634 | 995.36 | 17.6 | 7151.263
5.6634 | 1119.78 | 18.3833 | 8053.56
5.6634 | 1244.2 | 19.1333 | 9022.97
5.6634 | 1368.62 | 19.95 | 10066.95
5.6634 | 1493.04 | 20.7167 | 11110.93
5.6634 | 1617.46 | 21.45 | 12154.91
5.6634 | 1741.88 | 22.1667 | 13273.46
6.1353 | 622.1 | 15.6333 | 5234.814
6.1353 | 746.52 | 16.5 | 6077.455
6.1353 | 870.94 | 17.3 | 6935.01
6.1353 | 995.36 | 18.05 | 7829.85
6.1353 | 1119.78 | 18.7833 | 8724.69
6.1353 | 1244.2 | 19.5167 | 9694.1
6.1353 | 1368.62 | 20.2167 | 10663.51
6.1353 | 1493.04 | 20.9333 | 11707.49
6.1353 | 1617.46 | 21.6667 | 12826.04
6.1353 | 1741.88 | 22.3833 | 14019.16
6.6073 | 622.1 | 16.15 | 5823.917
6.6073 | 746.52 | 17 | 6718.757
6.6073 | 870.94 | 17.8 | 7606.14
6.6073 | 995.36 | 18.55 | 8575.55
6.6073 | 1119.78 | 19.25 | 9470.39
6.6073 | 1244.2 | 19.9333 | 10439.8
6.6073 | 1368.62 | 20.6167 | 11483.78
6.6073 | 1493.04 | 21.2833 | 12527.76
6.6073 | 1617.46 | 21.9167 | 13571.74
6.6073 | 1741.88 | 22.6 | 14764.86
7.0792 | 622.1 | 16.6667 | 6465.219
7.0792 | 746.52 | 17.5167 | 7412.258
7.0792 | 870.94 | 18.3 | 8351.84
7.0792 | 995.36 | 19.05 | 9321.25
7.0792 | 1119.78 | 19.75 | 10365.23
7.0792 | 1244.2 | 20.4167 | 11334.64
7.0792 | 1368.62 | 21.05 | 12378.62
7.0792 | 1493.04 | 21.6833 | 13422.6
7.0792 | 1617.46 | 22.3167 | 14541.15
7.0792 | 1741.88 | 22.9333 | 15659.7
7.5512 | 622.1 | 17.25 | 7151.263
7.5512 | 746.52 | 18.0333 | 8128.13
7.5512 | 870.94 | 18.8167 | 9172.11
7.5512 | 995.36 | 19.55 | 10216.09
7.5512 | 1119.78 | 20.25 | 11260.07
7.5512 | 1244.2 | 20.9 | 12304.05
7.5512 | 1368.62 | 21.55 | 13348.03
7.5512 | 1493.04 | 22.15 | 14466.58
7.5512 | 1617.46 | 22.7333 | 15510.56
7.5512 | 1741.88 | 23.35 | 16703.68
8.0231 | 622.1 | 17.85 | 7904.42
8.0231 | 746.52 | 18.6 | 8948.4
8.0231 | 870.94 | 19.3333 | 9992.38
8.0231 | 995.36 | 20.0667 | 11110.93
8.0231 | 1119.78 | 20.75 | 12229.48
8.0231 | 1244.2 | 21.4167 | 13273.46
8.0231 | 1368.62 | 22.0333 | 14392.01
8.0231 | 1493.04 | 22.65 | 15510.56
8.0231 | 1617.46 | 23.2333 | 16703.68
8.0231 | 1741.88 | 23.7833 | 17822.23
8.4951 | 622.1 | 18.4667 | 8724.69
8.4951 | 746.52 | 19.1833 | 9843.24
8.4951 | 870.94 | 19.8667 | 10961.79
8.4951 | 995.36 | 20.5833 | 12080.34
8.4951 | 1119.78 | 21.2667 | 13198.89
8.4951 | 1244.2 | 21.9167 | 14392.01
8.4951 | 1368.62 | 22.5333 | 15510.56
8.4951 | 1493.04 | 23.1333 | 16703.68
8.4951 | 1617.46 | 23.7167 | 17896.8
8.4951 | 1741.88 | 24.2833 | 19089.92
8.967 | 622.1 | 19.0833 | 9544.96
8.967 | 746.52 | 19.7833 | 10738.08
8.967 | 870.94 | 20.4667 | 11931.2
8.967 | 995.36 | 21.1 | 13124.32
8.967 | 1119.78 | 21.7833 | 14317.44
8.967 | 1244.2 | 22.4333 | 15510.56
8.967 | 1368.62 | 23.05 | 16703.68
8.967 | 1493.04 | 23.65 | 17971.37
8.967 | 1617.46 | 24.2167 | 19164.49
8.967 | 1741.88 | 24.7667 | 20432.18
9.4389 | 622.1 | 19.7333 | 10439.8
9.4389 | 746.52 | 20.4 | 11707.49
9.4389 | 870.94 | 21.0667 | 12975.18
9.4389 | 995.36 | 21.6833 | 14168.3
9.4389 | 1119.78 | 22.3 | 15435.99
9.4389 | 1244.2 | 22.95 | 16703.68
9.4389 | 1368.62 | 23.5667 | 17971.37
9.4389 | 1493.04 | 24.15 | 19239.06
9.4389 | 1617.46 | 24.7167 | 20581.32
9.4389 | 1741.88 | 25.2833 | 21849.01
9.9109 | 622.1 | 20.3667 | 11409.21
9.9109 | 746.52 | 21.0333 | 12751.47
9.9109 | 870.94 | 21.6667 | 14093.73
9.9109 | 995.36 | 22.2833 | 15361.42
9.9109 | 1119.78 | 22.8833 | 16703.68
9.9109 | 1244.2 | 23.4667 | 17971.37
9.9109 | 1368.62 | 24.0833 | 19313.63
9.9109 | 1493.04 | 24.6667 | 20655.89
9.9109 | 1617.46 | 25.2333 | 21998.15
9.9109 | 1741.88 | 25.7833 | 23340.41
10.3828 | 622.1 | 21.0333 | 12453.19
10.3828 | 746.52 | 21.6667 | 13870.02
10.3828 | 870.94 | 22.2833 | 15212.28
10.3828 | 995.36 | 22.8833 | 16629.11
10.3828 | 1119.78 | 23.4667 | 17971.37
10.3828 | 1244.2 | 24.0333 | 19313.63
10.3828 | 1368.62 | 24.6 | 20730.46
10.3828 | 1493.04 | 25.1833 | 22147.29
10.3828 | 1617.46 | 25.75 | 23489.55
10.3828 | 1741.88 | 26.2833 | 24906.38
10.8548 | 622.1 | 21.7 | 13646.31
10.8548 | 746.52 | 22.3167 | 14988.57
10.8548 | 870.94 | 22.9167 | 16479.97
10.8548 | 995.36 | 23.5 | 17896.8
10.8548 | 1119.78 | 24.0667 | 19313.63
10.8548 | 1244.2 | 24.6333 | 20730.46
10.8548 | 1368.62 | 25.1667 | 22221.86
10.8548 | 1493.04 | 25.7167 | 23638.69
10.8548 | 1617.46 | 26.2667 | 25130.09
10.8548 | 1741.88 | 26.8 | 26546.92
11.3267 | 622.1 | 22.3667 | 14839.43
11.3267 | 746.52 | 22.9667 | 16256.26
11.3267 | 870.94 | 23.55 | 17747.66
11.3267 | 995.36 | 24.1333 | 19239.06
11.3267 | 1119.78 | 24.6833 | 20805.03
11.3267 | 1244.2 | 25.2333 | 22296.43
11.3267 | 1368.62 | 25.7667 | 23787.83
11.3267 | 1493.04 | 26.2667 | 25279.23
11.3267 | 1617.46 | 26.8 | 26770.63
11.3267 | 1741.88 | 27.3333 | 28262.03
11.7987 | 622.1 | 23.05 | 16181.69
11.7987 | 746.52 | 23.6333 | 17673.09
11.7987 | 870.94 | 24.2 | 19164.49
11.7987 | 995.36 | 24.7667 | 20730.46
11.7987 | 1119.78 | 25.3 | 22296.43
11.7987 | 1244.2 | 25.8333 | 23862.4
11.7987 | 1368.62 | 26.35 | 25428.37
11.7987 | 1493.04 | 26.8667 | 26919.77
11.7987 | 1617.46 | 27.35 | 28560.31
11.7987 | 1741.88 | 27.85 | 30126.28
Note on A2: Data group describing grid variables for continuous fan performance
Note on C2: Data group describing lookup variables for continuous fan performance
Note on A3: Volumetric air flow rate through fan assembly at standard air conditions
Note on B3: External static pressure across fan assembly at dry coil conditions
Note on C3: Rotational speed of fan impeller
Note on D3: Mechanical shaft power input to fan assembly