## RS0003
RS0003: Fan Assembly
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0003 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | 1200 cfm Electronically Commutated Motor (ECM) fan (0.300 W/cfm @ 0.50 in. H2O) |  | ✓
| id | d12dc5a9-f8bc-4190-9286-c4096ec8ea2f |  | ✓
| data_timestamp | 2022-11-23T11:45Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/resdx
| disclaimer | This data is synthetic and does not represent any physical products.
performance |  |  |  | ✓
| nominal_standard_air_volumetric_flow_rate | 0.56634 | m3/s | ✓
| is_enclosed | TRUE |  | ✓
performance.assembly_components |  | $assembly_components
| heat_loss_fraction | 1 | - | ✓
| maximum_impeller_rotational_speed | 25 | rev/s | ✓
| minimum_impeller_rotational_speed | 0 | rev/s | ✓
| operation_speed_control_type | DISCRETE |  | ✓
| installation_speed_control_type | FIXED |  | ✓
performance.motor_representation |  | $motor_representation
performance.performance_map |  | $performance_map |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on A13: Data group containing performance information
Note on B14: Nominal or rated air flow rate at standard air conditions
Note on B15: Fan assembly is enclosed
Note on A16: An array of components included in the fan assembly air stream, not including any fans
Note on B17: Fraction of efficiency losses transferred into the air stream
Note on B18: Maximum impeller rotational speed
Note on B19: Minimum impeller rotational speed
Note on B20: Type of performance map
Note on B21: Type of fan impeller speed control
Note on A22: The corresponding Standard 205 motor representation
Note on A23: Data group describing fan assembly performance when operating

## assembly_components
performance.assembly_components
component_type | wet_pressure_difference
Pa
COIL | 75
Note on A2: Type of component
Note on B2: Additional static pressure difference if the component is wet (e.g., because of condensate collection or wetting evaporative media)

## motor_representation
performance.motor_representation
Data Group | Data Element | Value | Units | Required
performance.motor_representation.metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0005 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | Placeholder motor representation (performance characterized in parent RS0003 fan assembly) |  | ✓
| id | 48511b7d-9a5b-4dcc-b021-16ae6bf99d87 |  | ✓
| data_timestamp | 2022-11-23T11:45Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/resdx
| disclaimer | This data is synthetic and does not represent any physical products.
performance.motor_representation.performance |  |  |  | ✓
| maximum_power | 670.2203 | W | ✓
| standby_power | 0 | W | ✓
| number_of_poles | 6 |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on A13: Data group containing performance information
Note on B14: Maximum operational input power to the motor
Note on B15: Power draw when motor is not operating
Note on B16: Number of poles

## performance_map
performance.performance_map
grid_variables |  | lookup_variables
speed_number | static_pressure_difference | shaft_power | standard_air_volumetric_flow_rate | impeller_rotational_speed
- | Pa | W | m3/s | rev/s
1 | 0 | 68.8381 | 0.3875 | 9.9011
1 | 59.7797 | 115.1456 | 0.3875 | 11.1697
1 | 119.5593 | 161.4532 | 0.3875 | 12.4382
1 | 179.339 | 207.7607 | 0.3875 | 13.7067
1 | 239.1187 | 254.0682 | 0.3875 | 14.9753
1 | 298.8983 | 300.3758 | 0.3875 | 16.2438
2 | 0 | 68.8381 | 0.3875 | 9.9011
2 | 59.7797 | 115.1456 | 0.3875 | 11.1697
2 | 119.5593 | 161.4532 | 0.3875 | 12.4382
2 | 179.339 | 207.7607 | 0.3875 | 13.7067
2 | 239.1187 | 254.0682 | 0.3875 | 14.9753
2 | 298.8983 | 300.3758 | 0.3875 | 16.2438
3 | 0 | 83.1922 | 0.41256 | 10.5416
3 | 59.7797 | 132.4953 | 0.41256 | 11.8922
3 | 119.5593 | 181.7983 | 0.41256 | 13.2428
3 | 179.339 | 231.1014 | 0.41256 | 14.5934
3 | 239.1187 | 280.4045 | 0.41256 | 15.944
3 | 298.8983 | 329.7075 | 0.41256 | 17.2946
4 | 0 | 83.1922 | 0.41256 | 10.5416
4 | 59.7797 | 132.4953 | 0.41256 | 11.8922
4 | 119.5593 | 181.7983 | 0.41256 | 13.2428
4 | 179.339 | 231.1014 | 0.41256 | 14.5934
4 | 239.1187 | 280.4045 | 0.41256 | 15.944
4 | 298.8983 | 329.7075 | 0.41256 | 17.2946
5 | 0 | 210.0557 | 0.55784 | 14.2538
5 | 59.7797 | 276.7205 | 0.55784 | 16.08
5 | 119.5593 | 343.3853 | 0.55784 | 17.9062
5 | 179.339 | 410.0501 | 0.55784 | 19.7323
5 | 239.1187 | 476.7149 | 0.55784 | 21.5585
5 | 298.8983 | 543.3797 | 0.55784 | 23.3847
6 | 0 | 210.0557 | 0.55784 | 14.2538
6 | 59.7797 | 276.7205 | 0.55784 | 16.08
6 | 119.5593 | 343.3853 | 0.55784 | 17.9062
6 | 179.339 | 410.0501 | 0.55784 | 19.7323
6 | 239.1187 | 476.7149 | 0.55784 | 21.5585
6 | 298.8983 | 543.3797 | 0.55784 | 23.3847
7 | 0 | 220.1169 | 0.56634 | 14.4708
7 | 59.7797 | 287.7969 | 0.56634 | 16.3248
7 | 119.5593 | 355.4769 | 0.56634 | 18.1788
7 | 179.339 | 423.1569 | 0.56634 | 20.0328
7 | 239.1187 | 490.8369 | 0.56634 | 21.8868
7 | 298.8983 | 558.5169 | 0.56634 | 23.7408
8 | 0 | 220.1169 | 0.56634 | 14.4708
8 | 59.7797 | 287.7969 | 0.56634 | 16.3248
8 | 119.5593 | 355.4769 | 0.56634 | 18.1788
8 | 179.339 | 423.1569 | 0.56634 | 20.0328
8 | 239.1187 | 490.8369 | 0.56634 | 21.8868
8 | 298.8983 | 558.5169 | 0.56634 | 23.7408
Note on A2: Data group describing grid variables for continuous fan performance
Note on C2: Data group describing lookup variables for continuous fan performance
Note on A3: Number indicating discrete speed of fan impeller in rank order (with 1 being the lowest speed)
Note on B3: External static pressure across fan assembly at dry coil conditions
Note on C3: Mechanical shaft power input to fan assembly
Note on D3: Volumetric air flow rate through fan assembly at standard air conditions
Note on E3: Rotational speed of fan impeller