## RS0002
RS0002: Unitary Cooling Air-Conditioning Equipment
Data Group | Data Element | Value | Units | Required
ASHRAE205 |  |  |  | ✓
| RS_ID | RS0002 |  | ✓
| schema_version | 0.1.0 |  | ✓
| ID | bcf8b859-67a3-42f4-8f8d-4e57af1ccf22 |  | ✓
| data_timestamp | 2019-09-13T00:00Z |  | ✓
| data_version | A205DV-1
| description | Simple Example File
| data_source | Committee
| notes | This is a simple example of a JSON file for RS0002 - this file should not be used for simulation
ASHRAE205.RS_instance |  |  |  | ✓
ASHRAE205.RS_instance.RS0002
ASHRAE205.RS_instance.RS0002.description
ASHRAE205.RS_instance.RS0002.description.product_information
| outdoor_unit_manufacturer | ColdAirInc |  | ✓
| outdoor_unit_model_number | AC.2019.01 |  | ✓
| indoor_unit_manufacturer | ColdAirInc
| indoor_unit_model_number | AC.2019.02
| refrigerant_type | R410A
| compressor_type | SCROLL
ASHRAE205.RS_instance.RS0002.performance |  |  |  | ✓
| compressor_control_method | DYNAMIC |  | ✓
| fan_position | BLOW_THROUGH |  | ✓
| nominal_volumetric_air_flow_rate | 0.59 | m3/s | ✓
| cycling_degradation_coefficient | 0.25 |  | ✓
ASHRAE205.RS_instance.RS0002.performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
ASHRAE205.RS_instance.RS0002.performance.performance_map_standby |  | $performance_map_standby |  | ✓

## performance_map_cooling
ASHRAE205.RS_instance.RS0002.performance.performance_map_cooling.grid_variables
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_wet_bulb_temperature | indoor_coil_entering_dry_bulb_temperature | indoor_coil_volumetric_flow_ratio | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_cooling_capacity | gross_sensible_cooling_capacity | gross_cooling_power
K | K | K | - |  | Pa | W | W | W
302.55 | 288.15 | 300.15 | 0.72 | 1 | 101.325 | 3.2 | 3.2 | 0.52
302.55 | 288.15 | 300.15 | 1 | 1 | 101.325 | 3.6 | 3.6 | 0.48
302.55 | 288.15 | 302.15 | 0.72 | 1 | 101.325 | 3.2 | 3.2 | 0.52
302.55 | 288.15 | 302.15 | 1 | 1 | 101.325 | 3.6 | 3.6 | 0.48
302.55 | 290.35 | 300.15 | 0.72 | 1 | 101.325 | 3.2 | 3.2 | 0.52
302.55 | 290.35 | 300.15 | 1 | 1 | 101.325 | 3.6 | 3.6 | 0.48
302.55 | 290.35 | 302.15 | 0.72 | 1 | 101.325 | 3.2 | 3.2 | 0.52
302.55 | 290.35 | 302.15 | 1 | 1 | 101.325 | 3.6 | 3.6 | 0.48
302.55 | 292.55 | 300.15 | 0.72 | 1 | 101.325 | 3.4 | 2.788 | 0.5
302.55 | 292.55 | 300.15 | 1 | 1 | 101.325 | 3.6 | 3.348 | 0.47
302.55 | 292.55 | 302.15 | 0.72 | 1 | 101.325 | 3.4 | 3.332 | 0.5
302.55 | 292.55 | 302.15 | 1 | 1 | 101.325 | 3.6 | 3.6 | 0.47
308.15 | 288.15 | 300.15 | 0.72 | 1 | 101.325 | 3 | 3 | 0.64
308.15 | 288.15 | 300.15 | 1 | 1 | 101.325 | 3 | 3 | 0.62
308.15 | 288.15 | 302.15 | 0.72 | 1 | 101.325 | 3 | 3 | 0.64
308.15 | 288.15 | 302.15 | 1 | 1 | 101.325 | 3 | 3 | 0.62
308.15 | 290.35 | 300.15 | 0.72 | 1 | 101.325 | 3 | 3 | 0.65
308.15 | 290.35 | 300.15 | 1 | 1 | 101.325 | 3 | 3 | 0.61
308.15 | 290.35 | 302.15 | 0.72 | 1 | 101.325 | 3 | 3 | 0.65
308.15 | 290.35 | 302.15 | 1 | 1 | 101.325 | 3 | 3 | 0.61
308.15 | 292.55 | 300.15 | 0.72 | 1 | 101.325 | 3.1 | 2.666 | 0.63
308.15 | 292.55 | 300.15 | 1 | 1 | 101.325 | 3.1 | 3.038 | 0.61
308.15 | 292.55 | 302.15 | 0.72 | 1 | 101.325 | 3.1 | 3.1 | 0.63
308.15 | 292.55 | 302.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.61
313.75 | 288.15 | 300.15 | 0.72 | 1 | 101.325 | 2.8 | 2.8 | 0.79
313.75 | 288.15 | 300.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76
313.75 | 288.15 | 302.15 | 0.72 | 1 | 101.325 | 2.8 | 2.8 | 0.79
313.75 | 288.15 | 302.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76
313.75 | 290.35 | 300.15 | 0.72 | 1 | 101.325 | 2.8 | 2.8 | 0.79
313.75 | 290.35 | 300.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76
313.75 | 290.35 | 302.15 | 0.72 | 1 | 101.325 | 2.8 | 2.8 | 0.79
313.75 | 290.35 | 302.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76
313.75 | 292.55 | 300.15 | 0.72 | 1 | 101.325 | 2.9 | 2.61 | 0.78
313.75 | 292.55 | 300.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76
313.75 | 292.55 | 302.15 | 0.72 | 1 | 101.325 | 2.9 | 2.9 | 0.78
313.75 | 292.55 | 302.15 | 1 | 1 | 101.325 | 3.1 | 3.1 | 0.76

## performance_map_standby
ASHRAE205.RS_instance.RS0002.performance.performance_map_standby.grid_variables
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
255.37 | 40
283.15 | 40
283.65 | 0
310.93 | 0