## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
| schema_version | 0.1.0 |  | ✓
| standard_version | PPR2 |  | ✓
| RS_ID | RS0001 |  | ✓
| description | Water-Cooled Chiller with Constant Efficiency |  | ✓
| ID | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 5.9
RS_instance |  |  |  | ✓
RS_instance.description
RS_instance.description.product_information
| manufacturer | ABC Chillers |  | ✓
| model_number | Chiller A1B2 |  | ✓
| nominal_voltage | 460 | V
| nominal_frequency | 60 | Hz
| compressor_type | CENTRIFUGAL
| speed_control_type | CONSTANT_SPEED
| liquid_data_source | AHRI_550_590_2015
| refrigerant_type | R134A
| hotgas_bypass_installed | FALSE
RS_instance.performance
RS_instance.performance.evaporator_liquid_type |  |  |  | ✓
RS_instance.performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
RS_instance.performance.condenser_liquid_type |  |  |  | ✓
RS_instance.performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0.01761 | m2-K/W | ✓
| condenser_fouling_factor | 0.04403 | m2-K/W | ✓
| unit_power_limit | 31400 | W
| cycling_degradation_coefficient | 0.25 | - | ✓
RS_instance.performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
RS_instance.performance.performance_map_standby |  | $performance_map_standby |  | ✓

## liquid_components
RS_instance.performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1

## liquid_components0
RS_instance.performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1

## performance_map_cooling
RS_instance.performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | net_evaporator_capacity_fraction | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | motor_controller_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.0755 | 279.82 | 0.0957 | 294.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 295.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 296.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 297.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 298.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 299.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 298.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 299.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 300.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 301.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 302.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 301.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 302.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 303.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 304.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 305.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 303.6199 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 304.6498 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 305.6797 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 306.7095 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 307.7394 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 295.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 296.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 297.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 298.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 299.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 298.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 299.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 300.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 301.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 302.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 301.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 302.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 303.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 304.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 305.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 0.2 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 303.6199 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 0.4 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 304.6498 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 0.6 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 305.6797 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 0.8 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 306.7095 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 1 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 307.7394 | 74400 | 23600 | 0 | 0

## performance_map_standby
RS_instance.performance.performance_map_standby
grid_variables | lookup_variables
chiller_environment_dry_bulb_temperature | input_power
K | W
273.15 | 2200
311.15 | 2200